## 6700SS
IntelliKnight 6700 Battery Calculation
| Secondary Power Source Requirements | [10 empty] | 5 Minutes | 0.084 | 24 Hours | 24
[12 empty] | 10 Minutes | 0.167 | 48 Hours | 48
| Standby Current (amps) |  |  |  |  | Secondary Alarm Current (amps) | [5 empty] | 15 Minutes | 0.25 | 60 Hours | 60
Device Type | Qty | Current Draw |  |  | Total | Qty | Current Draw |  |  | Total |  | 20 Minutes | 0.334 | 72 Hours | 72
1. Control Panel | [11 empty] | 25 Minutes | 0.417 | 90 Hours | 90
6700 Control Panel | 1 | x | 0.165 | = | 0.165 | 1 | x | 0.31 | = | 0.31 |  | 30 Minutes | 0.5 | 96 Hours | 96
2. Addressable SLC Devices | [11 empty] | 45 Minutes | 0.75 | 120 Hours | 120
SK-PHOTO (-T) |  | x | 0.0003 | = |  | 0 | x | 0.0003 | = |  |  | 60 Minutes | 1
SK-PHOTO-W (-T) |  | x | 0.0002 | = |  | 0 | x | 0.00045 | = |  |  | 90 Minutes | 1.5
SK-HEAT(-HT) (-ROR) |  | x | 0.0003 | = |  | 0 | x | 0.0003 | = |  |  | 120 Minutes | 2
SK-HEAT-W(HT) (ROR) |  | x | 0.0002 | = |  | 0 | x | 0.00045 | = |  |  | 180 Minutes | 3
SK-BEAM |  | x | 0.002 | = |  | 0 | x | 0.002 | =
SK-BEAM-T |  | x | 0.002 | = |  | 0 | x | 0.002 | =
SK-DUCT |  | x | 0.0003 | = |  | 0 | x | 0.0003 | =
SK-ACCLIMATE |  | x | 0.0003 | = |  | 0 | x | 0.0003 | =
SK-CONTROL |  | x | 0.000375 | = |  | 0 | x | 0.000375 | =
SK-MONITOR |  | x | 0.000375 | = |  | 0 | x | 0.000375 | =
SK-MINIMON |  | x | 0.000375 | = |  | 0 | x | 0.000375 | =
SK-PULL-SA |  | x | 0.000375 | = |  | 0 | x | 0.000375 | =
SK-PULL-DA |  | x | 0.000375 | = |  | 0 | x | 0.000375 | =
SK-MONITOR-2 |  | x | 0.00075 | = |  | 0 | x | 0.00075 | =
SK-MON-10 |  | x | 0.0035 | = |  | 0 | x | 0.0035 | =
SK-RELAY-6 |  | x | 0.00145 | = |  | 0 | x | 0.00145 | =
SK-CONTROL-6 |  | x | 0.00225 | = |  | 0 | x | 0.00225 | =
SK-RELAY |  | x | 0.000255 | = |  | 0 | x | 0.000255 | =
SK-RELAYMON-2 |  | x | 0.0013 | = |  | 0 | x | 0.024 | =
SK-ZONE |  | x | 0.00027 | = |  | 0 | x | 0.00027 | =
SK-ZONE-6 |  | x | 0.002 | = |  | 0 | x | 0.002 | =
SK-FIRE-CO |  | x | 0.0003 | = |  | 0 | x | 0.0072 | =
3. SLC Accessory Bases
B200S |  | x | 0.0003 | = |  | 0 | x | 0.0003 | =
B200S-LF |  | x | 0.0003 | = |  | 0 | x | 0.0003 | =
B200SR |  | x | 0.0003 | = |  | 0 | x | 0.0003 | =
B200SR-LF |  | x | 0.0003 | = |  | 0 | x | 0.0003 | =
B224RB |  | x | 0.0005 | = |  | 0 | x | 0.0005 | =
RTS151 |  | x | 0 | = |  | 0 | x | 0.0075 | =
RTS151KEY |  | x | 0 | = |  | 0 | x | 0.0075 | =
RA100Z |  | x | 0 | = |  | 0 | x | 0.01 | =
4. SLC Isolator Devices
SK-ISO |  | x | 0.00045 | = |  | 0 | x | 0.00045 | =
ISO-6 |  | x | 0.0027 | = |  | 0 | x | 0.102 | =
B224BI |  | x | 0.0005 | = |  | 0 | x | 0.0005 | =
5. Auxiliary Power Draw - SLC Devices
SK-CONTROL (Aux. Power) |  | x | 0.0017 | = |  | 0 | x | 0.007 | =
SK-CONTROL-6 (Aux. Power) |  | x | 0.008 | = |  | 0 | x | 0.02 | =
SK-ZONE (Aux. Power) |  | x | 0.012 | = |  | 0 | x | 0.09 | =
SK-ZONE-6 (Aux. Power) |  | x | 0.05 | = |  | 0 | x | 0.27 | =
B200S (Aux. Power) |  | x | 0.0005 | = |  | 0 | x | 0.035 | =
B200S-LF (Aux. Power) |  | x | 0.00055 | = |  | 0 | x | 0.14 | =
B200SR (Aux. Power) |  | x | 0.0005 | = |  | 0 | x | 0.035 | =
B200SR-LF (Aux. Power) |  | x | 0.001 | = |  | 0 | x | 0.125 | =
6. Accessory Modules
5860 |  | x | 0.02 | = |  | 0 | x | 0.025 | =
5824 |  | x | 0.045 | = |  | 0 | x | 0.045 | =
5496 |  | x | 0.01 | = |  | 0 | x | 0.01 | =
5895XL |  | x | 0.01 | = |  | 0 | x | 0.01 | =
6855 |  | x | 0.02 | = |  | 0 | x | 0.025 | =
6860 |  | x | 0.025 | = |  | 0 | x | 0.05 | =
5865-4 |  | x | 0.035 | = |  | 0 | x | 0.145 | =
5865-3 |  | x | 0.035 | = |  | 0 | x | 0.145 | =
5880 |  | x | 0.035 | = |  | 0 | x | 0.2 | =
5883 |  | x | 0 | = |  | 0 | x | 0.22 | =
SK-IP-2 |  | x | 0.093 | = |  | 0 | x | 0.136 | =
SK-IP-2UD |  | x | 0.098 | = |  | 0 | x | 0.155 | =
CELL-MOD |  | x | 0.055 | = |  | 0 | x | 0.1 | =
CELL-CAB-SK |  | x | 0.055 | = |  | 0 | x | 0.1 | =
WSK-WGI Aux. Power |  | x | 0.04 | = |  | 0 | x | 0.04 | =
SLC Power |  | x | 0.024 | = |  | 0 | x | 0.024 | =
SK-NIC |  | x | 0.021 | = |  | 0 | x | 0.021 | =
SK-NIC-KIT |  | x | 0.021 | = |  | 0 | x | 0.021 | =
SK-FSL |  | x | 0.079 | = |  | 0 | x | 0.079 | =
SK-FML |  | x | 0.053 | = |  | 0 | x | 0.053 | =
SK-FFT |  | x | 0.12 | = |  | 0 | x | 0.23 | =
7. Miscellaneous Devices
Conventional Detectors | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 1 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 2 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 3 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 4 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 5 | 0 | x | 0 | = |  | 0 | x | 0 | =
8. Notification Appliance Circuits
NAC 1 |  |  | 0 | = |  |  |  | 0 | =
NAC 2 |  |  | 0 | = |  |  |  | 0 | =
Total Standby Load |  |  |  |  | 0.165 | Total Alarm Load |  |  |  | 0.31
IntelliKnight 6700 Battery Calculation
Note 1: You are fully responsible for verifying these calculations.
Note 2: Use the dropdowns in the yellow cells to enter values.
Calculation in Total Sheet
Required Standby Time in Hours
24 Hours
Standby Load Current |  |  | 0.165 |  |  | x | 24 |  | = | 3.96
Required Alarm Time in Minutes
5 Minutes
Alarm Load Current (Amps) |  |  | 0.31 |  |  | x | 0.084 |  | = | 0.02604
Total Current Load | [9 empty] | 3.986
Multiply by the Derating Factor | [5 empty] | 1.2 |  |  | = | 1.2
Total Ampere Hours Required | [9 empty] | 4.7832
Recommended Batteries: | [5 empty] | BAT-1270 - 7AH Batteries
Battery Check
The batteries can be charged by the 6700 Charger.
The batteries can be housed in the 6700 Cabinet.
Current Draw Check
Circuit#1 current is within the limitations of the circuit.
Circuit#2 current is within the limitations of the circuit.
6700 Control Panel:
The output current is within the panel's limitations.
IntelliKnight 6700 Circuit Detail
NAC 1
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
|  | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
NAC 2
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
IntelliKnight 6700 EOL Voltage Drop
Starting Voltage | 20.4
Minimum Voltage @ EOL | 16
Voltage Drop Warning % | 10%
| Current Draw |  | Wire Type | Resistance |  | Length |  | Actual Resistance | Voltage @ EOL |  | Percent Drop
Circuit Name | Amps |  | AWG | Ohms/1000 ft. |  | Feet (One Way) |  | Ohms | Volts |  | Percent
NAC 1 | 0 |  | #12 Solid | 1.93 |  | 0 |  | 0 | 20.4 |  | 0%
NAC 2 | 0 |  | #12 Solid | 1.93 |  | 0 |  | 0 | 20.4 |  | 0%
Resistance Table
Wire Type |  | Resitance
AWG |  | Ohms/1000 ft.
#10 Solid |  | 1.21
#10 Stranded |  | 1.24
#12 Solid |  | 1.93
#12 Stranded |  | 1.98
#14 Solid |  | 3.07
#14 Stranded |  | 3.14
#16 Solid |  | 4.89
#16 Stranded |  | 4.99
#18 Solid |  | 7.77
#18 Stranded |  | 7.95
Note: All Resistance values are taken from Table 8 Conductor Properties of the NFPA 70 National Electrical Code. All values are for Direct Current Resistance at 75°C (167°F).
Note on H96: Select Standby Time in Hours from the dropdown list.
Note on H99: Select the Alarm Time in minutes from the dropdown list.
Note on H102: Select the Derating Factor from the dropdown list.

## 6700H
IntelliKnight 6700 Battery Calculation
| Secondary Power Source Requirements | [10 empty] | 5 Minutes | 0.084 | 24 Hours | 24
[12 empty] | 10 Minutes | 0.167 | 48 Hours | 48
| Standby Current (amps) |  |  |  |  | Secondary Alarm Current (amps) | [5 empty] | 15 Minutes | 0.25 | 60 Hours | 60
Device Type | Qty | Current Draw |  |  | Total | Qty | Current Draw |  |  | Total |  | 20 Minutes | 0.334 | 72 Hours | 72
1. Control Panel | [11 empty] | 25 Minutes | 0.417 | 90 Hours | 90
6700 Control Panel | 1 | x | 0.165 | = | 0.165 | 1 | x | 0.31 | = | 0.31 |  | 30 Minutes | 0.5 | 96 Hours | 96
2. Addressable SLC Devices | [11 empty] | 45 Minutes | 0.75 | 120 Hours | 120
SD500-AIM | 0 | x | 0.0003 | = |  | 0 | x | 0.0003 | = |  |  | 60 Minutes | 1
SD500-MIM | 0 | x | 0.0003 | = |  | 0 | x | 0.0003 | = |  |  | 90 Minutes | 1.5
SD500-ARM | 0 | x | 0.0003 | = |  | 0 | x | 0.0003 | = |  |  | 120 Minutes | 2
SD500-PS | 0 | x | 0.0003 | = |  | 0 | x | 0.0003 | = |  |  | 180 Minutes | 3
SD500-PSDA | 0 | x | 0.0003 | = |  | 0 | x | 0.0003 | = |  |  | 240 minutes | 4
SD505-HEAT | 0 | x | 0.0003 | = |  | 0 | x | 0.0003 | =
SD505-PHOTO | 0 | x | 0.0003 | = |  | 0 | x | 0.0003 | =
SD505-DTS-K | 0 | x | 0 | = |  | 0 | x | 0 | =
SD500-ANM | 0 | x | 0.00055 | = |  | 0 | x | 0.00055 | =
SD500-SDM | 0 | x | 0.00055 | = |  | 0 | x | 0.00055 | =
SD505-DUCT | 0 | x | 0.0005 | = |  | 0 | x | 0.0005 | =
SD505-DUCTR | 0 | x | 0.0005 | = |  | 0 | x | 0.0005 | =
3. SLC Accessory Bases
SD505-4AB | 0 | x | 0 | = |  | 0 | x | 0 | =
SD505-6AB | 0 | x | 0 | = |  | 0 | x | 0 | =
SD505-6RB | 0 | x | 8.2e-05 | = |  | 0 | x | 8.2e-05 | =
SD505-6SB | 0 | x | 8.2e-05 | = |  | 0 | x | 8.2e-05 | =
4. SLC Isolator Devices
SD500-LIM | 0 | x | 9.2e-05 | = |  | 0 | x | 9.2e-05 | =
SD505-6IB | 0 | x | 9.2e-05 | = |  | 0 | x | 9.2e-05 | =
5. Auxiliary Power Draw - SLC Devices
SD500-ANM (Aux. Power) | 0 | x | 0.008 | = |  | 0 | x | 0.06 | =
SD500-SDM (Aux. Power) | 0 | x | 0.02 | = |  | 0 | x | 0.106 | =
SD500-LED (Aux. Power) | 0 | x | 0.01 | = |  | 0 | x | 0.22 | =
SD505-6SB (Aux. Power) | 0 | x | 0.001 | = |  | 0 | x | 0.032 | =
6. Accessory Modules
5860 |  | x | 0.02 | = |  | 0 | x | 0.025 | =
6860 |  | x | 0.025 | = |  | 0 | x | 0.05 | =
6855 |  | x | 0.02 | = |  | 0 | x | 0.025
5824 |  | x | 0.045 | = |  | 0 | x | 0.045 | =
5496 |  | x | 0.01 | = |  | 0 | x | 0.01 | =
5895XL |  | x | 0.01 | = |  | 0 | x | 0.01 | =
5865-4 |  | x | 0.035 | = |  | 0 | x | 0.145 | =
5865-3 |  | x | 0.035 | = |  | 0 | x | 0.145 | =
5880 |  | x | 0.035 | = |  | 0 | x | 0.2 | =
5883 |  | x | 0 | = |  | 0 | x | 0.22 | =
SK-IP-2 | 0 | x | 0.093 | = |  | 0 | x | 0.136 | =
SK-IP-2UD | 0 | x | 0.098 | = |  | 0 | x | 0.155 | =
CELL-MOD | 0 | x | 0.055 | = |  | 0 | x | 0.1 | =
CELL-CAB-SK | 0 | x | 0.055 | = |  | 0 | x | 0.1 | =
SK-NIC | 0 | x | 0.021 | = |  | 0 | x | 0.021 | =
SK-NIC-KIT | 0 | x | 0.021 | = |  | 0 | x | 0.021 | =
SK-FSL | 0 | x | 0.079 | = |  | 0 | x | 0.079 | =
SK-FML | 0 | x | 0.053 | = |  | 0 | x | 0.053 | =
SK-FFT | 0 | x | 0.12 | = |  | 0 | x | 0.23 | =
7. Miscellaneous Devices
Conventional Detectors | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 1 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 2 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 3 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 4 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 5 | 0 | x | 0 | = |  | 0 | x | 0 | =
8. Notification Appliance Circuits
NAC 1 |  |  | 0 | = |  |  |  | 0 | =
NAC 2 |  |  | 0 | = |  |  |  | 0 | =
Total Standby Load |  |  |  |  | 0.165 | Total Alarm Load |  |  |  | 0.31
IntelliKnight 6700 Battery Calculation
Note 1: You are fully responsible for verifying these calculations.
Note 2: Use the dropdowns in the yellow cells to enter values.
Calculation in Total Sheet
Required Standby Time in Hours
24 Hours
Standby Load Current |  |  | 0.165 |  |  | x | 24 |  | = | 3.96
Required Alarm Time in Minutes
5 Minutes
Alarm Load Current (Amps) |  |  | 0.31 |  |  | x | 0.084 |  | = | 0.02604
Total Current Load | [9 empty] | 3.986
Multiply by the Derating Factor | [5 empty] | 1.2 |  |  | = | 1.2
Total Ampere Hours Required | [9 empty] | 4.7832
Recommended Batteries: | [5 empty] | BAT-1270 - 7AH Batteries
Battery Check
The batteries can be charged by the 6700 Charger.
The batteries can be housed in the 6700 Cabinet.
Current Draw Check
Circuit#1 current is within the limitations of the circuit.
Circuit#2 current is within the limitations of the circuit.
6700 Control Panel:
The output current is within the panel's limitations.
IntelliKnight 6700 Circuit Detail
NAC 1
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
NAC 2
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
IntelliKnight 6700 EOL Voltage Drop
Starting Voltage | 20.4
Minimum Voltage @ EOL | 16
Voltage Drop Warning % | 10%
| Current Draw |  | Wire Type | Resistance |  | Length |  | Actual Resistance | Voltage @ EOL |  | Percent Drop
Circuit Name | Amps |  | AWG | Ohms/1000 ft. |  | Feet (One Way) |  | Ohms | Volts |  | Percent
NAC 1 | 0 |  | #12 Solid | 1.93 |  | 0 |  | 0 | 20.4 |  | 0
NAC 2 | 0 |  | #12 Solid | 1.93 |  | 0 |  | 0 | 20.4 |  | 0
Resistance Table
Wire Type |  | Resitance
AWG |  | Ohms/1000 ft.
#10 Solid |  | 1.21
#10 Stranded |  | 1.24
#12 Solid |  | 1.93
#12 Stranded |  | 1.98
#14 Solid |  | 3.07
#14 Stranded |  | 3.14
#16 Solid |  | 4.89
#16 Stranded |  | 4.99
#18 Solid |  | 7.77
#18 Stranded |  | 7.95
Note: All Resistance values are taken from Table 8 Conductor Properties of the NFPA 70 National Electrical Code. All values are for Direct Current Resistance at 75°C (167°F).
Note on H75: Select Standby Time in Hours from the dropdown list.
Note on H78: Select the Alarm Time in minutes from the dropdown list.
Note on H81: Select the Derating Factor from the dropdown list.

## 6808H
IntelliKnight 6808 Battery Calculation
| Secondary Power Source Requirements | [10 empty] | 5 Minutes | 0.084 | 24 Hours | 24
[12 empty] | 10 Minutes | 0.167 | 48 Hours | 48
| Standby Current (amps) |  |  |  |  | Secondary Alarm Current (amps) | [5 empty] | 15 Minutes | 0.25 | 60 Hours | 60
Device Type | Qty | Current Draw |  |  | Total | Qty | Current Draw |  |  | Total |  | 20 Minutes | 0.334 | 72 Hours | 72
1. Control Panel | [11 empty] | 25 Minutes | 0.417 | 90 Hours | 90
6808 Control Panel | 1 | x | 0.19 | = | 0.19 | 1 | x | 0.25 | = | 0.25 |  | 30 Minutes | 0.5 | 96 Hours | 96
2. Addressable SLC Devices | [11 empty] | 45 Minutes | 0.75 | 120 Hours | 120
SD500-AIM |  | x | 0.00055 | = |  | 0 | x | 0.00055 | = |  |  | 60 Minutes | 1
SD500-MIM |  | x | 0.00055 | = |  | 0 | x | 0.00055 | = |  |  | 90 Minutes | 1.5
SD500-ARM |  | x | 0.00055 | = |  | 0 | x | 0.00055 | = |  |  | 120 Minutes | 2
SD500-PS |  | x | 0.00055 | = |  | 0 | x | 0.00055 | = |  |  | 180 Minutes | 3
SD500-PSDA |  | x | 0.00055 | = |  | 0 | x | 0.00055 | = |  |  | 240 minutes | 4
SD505-HEAT |  | x | 0.00055 | = |  | 0 | x | 0.00055 | =
SD505-PHOTO |  | x | 0.00055 | = |  | 0 | x | 0.00055 | =
SD505-DTS |  | x | 0 | = |  | 0 | x | 0 | =
SD500-ANM |  | x | 0.00055 | = |  | 0 | x | 0.00055 | =
SD500-SDM |  | x | 0.00055 | = |  | 0 | x | 0.00055 | =
SD505-DUCT |  | x | 0.0005 | = |  | 0 | x | 0.0005 | =
SD505-DUCTR |  | x | 0.0005 | = |  | 0 | x | 0.0005 | =
3. SLC Accessory Bases
SD505-4AB |  | x | 0 | = |  | 0 | x | 0 | =
SD505-6AB |  | x | 0 | = |  | 0 | x | 0 | =
SD505-6RB |  | x | 8.2e-05 | = |  | 0 | x | 8.2e-05 | =
SD505-6SB |  | x | 8.2e-05 | = |  | 0 | x | 8.2e-05 | =
4. SLC Isolator Devices
SD500-LIM |  | x | 9.2e-05 | = |  | 0 | x | 9.2e-05 | =
SD505-6IB |  | x | 9.2e-05 | = |  | 0 | x | 9.2e-05 | =
5. Auxiliary Power Draw - SLC Devices
SD500-ANM (Aux. Power) |  | x | 0.008 | = |  | 0 | x | 0.06 | =
SD500-SDM (Aux. Power) |  | x | 0.02 | = |  | 0 | x | 0.106 | =
SD500-LED (Aux. Power) |  | x | 0.01 | = |  | 0 | x | 0.22 | =
SD505-6SB (Aux. Power) |  | x | 0.001 | = |  | 0 | x | 0.032 | =
6. Accessory Modules
5860 |  | x | 0.02 | = |  | 0 | x | 0.025 | =
6860 |  | x | 0.025 | = |  | 0 | x | 0.05 | =
6855 |  | x | 0.02 | = |  | 0 | x | 0.025 | =
5824 |  | x | 0.045 | = |  | 0 | x | 0.045 | =
5496 |  | x | 0.01 | = |  | 0 | x | 0.01 | =
5865-4 |  | x | 0.035 | = |  | 0 | x | 0.145 | =
5865-3 |  | x | 0.035 | = |  | 0 | x | 0.145 | =
5880 |  | x | 0.035 | = |  | 0 | x | 0.2 | =
5883 |  | x | 0 | = |  | 0 | x | 0.22 | =
SK-IP-2 |  | x | 0.093 | = |  | 0 | x | 0.136 | =
SK-IP-2UD |  | x | 0.098 | = |  | 0 | x | 0.155 | =
CELL-MOD |  | x | 0.055 | = |  | 0 | x | 0.1 | =
CELL-CAB-SK |  | x | 0.055 | = |  | 0 | x | 0.1 | =
SK-NIC |  | x | 0.021 | = |  | 0 | x | 0.021 | =
SK-NIC-KIT |  | x | 0.021 | = |  | 0 | x | 0.021 | =
SK-FSL |  | x | 0.079 | = |  | 0 | x | 0.079 | =
SK-FML |  | x | 0.053 | = |  | 0 | x | 0.053 | =
SK-FFT |  | x | 0.12 | = |  | 0 | x | 0.23 | =
7. Miscellaneous Devices
Conventional Detectors | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 1 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 2 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 3 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 4 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 5 | 0 | x | 0 | = |  | 0 | x | 0 | =
8. Notification Appliance Circuits
NAC 1 |  |  | 0 | = |  |  |  | 0 | =
NAC 2 |  |  | 0 | = |  |  |  | 0 | =
NAC 3 |  |  | 0 | = |  |  |  | 0 | =
NAC 4 |  |  | 0 | = |  |  |  | 0 | =
Total Standby Load |  |  |  |  | 0.19 | Total Alarm Load |  |  |  | 0.25
IntelliKnight 6808 Battery Calculation
Note 1: You are fully responsible for verifying these calculations.
Note 2: Use the dropdowns in the yellow cells to enter values.
Calculation in Total Sheet
Required Standby Time in Hours
24 Hours
Standby Load Current |  |  | 0.19 |  |  | x | 24 |  | = | 4.56
Required Alarm Time in Minutes
5 Minutes
Alarm Load Current (Amps) |  |  | 0.25 |  |  | x | 0.084 |  | = | 0.021
Total Current Load | [9 empty] | 4.581
Multiply by the Derating Factor | [5 empty] | 1.2 |  |  | = | 1.2
Total Ampere Hours Required | [9 empty] | 5.4972
Recommended Batteries: | [5 empty] | BAT-1270 - 7AH Batteries
Battery Check
The batteries can be charged by the 6808 Charger.
The batteries can be housed in the 6808 Cabinet.
Current Draw Check
Circuit#1 current is within the limitations of the circuit.
Circuit#2 current is within the limitations of the circuit.
Circuit#3 current is within the limitations of the circuit.
Circuit#4 current is within the limitations of the circuit.
6808 Control Panel:
The output current is within the panel's limitations.
IntelliKnight 6808 Circuit Detail
NAC 1
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
NAC 2
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
NAC 3
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
NAC 4
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
IntelliKnight 6808 EOL Voltage Drop
Starting Voltage | 20.4
Minimum Voltage @ EOL | 16
Voltage Drop Warning % | 10%
| Current Draw |  | Wire Type | Resistance |  | Length |  | Actual Resistance | Voltage @ EOL |  | Percent Drop
Circuit Name | Amps |  | AWG | Ohms/1000 ft. |  | Feet (One Way) |  | Ohms | Volts |  | Percent
NAC 1 | 0 |  | #12 Solid | 1.93 |  | 0 |  | 0 | 20.4 |  | 0%
NAC 2 | 0 |  | #12 Solid | 1.93 |  | 0 |  | 0 | 20.4 |  | 0%
NAC 3 | 0 |  | #12 Solid | 1.93 |  | 0 |  | 0 | 20.4 |  | 0%
NAC 4 | 0 |  | #12 Solid | 1.93 |  | 0 |  | 0 | 20.4 |  | 0%
Resistance Table
Wire Type |  | Resitance
AWG |  | Ohms/1000 ft.
#10 Solid |  | 1.21
#10 Stranded |  | 1.24
#12 Solid |  | 1.93
#12 Stranded |  | 1.98
#14 Solid |  | 3.07
#14 Stranded |  | 3.14
#16 Solid |  | 4.89
#16 Stranded |  | 4.99
#18 Solid |  | 7.77
#18 Stranded |  | 7.95
Note: All Resistance values are taken from Table 8 Conductor Properties of the NFPA 70 National Electrical Code. All values are for Direct Current Resistance at 75°C (167°F).
Note on H76: Select Standby Time in Hours from the dropdown list.
Note on H79: Select the Alarm Time in minutes from the dropdown list.
Note on H82: Select the Derating Factor from the dropdown list.

## 6808SS
IntelliKnight 6808 Battery Calculation
| Secondary Power Source Requirements | [10 empty] | 5 Minutes | 0.084 | 24 Hours | 24
[12 empty] | 10 Minutes | 0.167 | 48 Hours | 48
| Standby Current (amps) |  |  |  |  | Secondary Alarm Current (amps) | [5 empty] | 15 Minutes | 0.25 | 60 Hours | 60
Device Type | Qty | Current Draw |  |  | Total | Qty | Current Draw |  |  | Total |  | 20 Minutes | 0.334 | 72 Hours | 72
1. Control Panel | [11 empty] | 25 Minutes | 0.417 | 90 Hours | 90
6808 Control Panel | 1 | x | 0.19 | = | 0.19 | 1 | x | 0.25 | = | 0.25 |  | 30 Minutes | 0.5 | 96 Hours | 96
2. Addressable SLC Devices | [11 empty] | 45 Minutes | 0.75 | 120 Hours | 120
SK-PHOTO (-T) |  | x | 0.0003 | = |  | 0 | x | 0.0003 | = |  |  | 60 Minutes | 1
SK-PHOTO-W (-T) |  | x | 0.0002 | = |  | 0 | x | 0.00045 | = |  |  | 90 Minutes | 1.5
SK-HEAT(-HT) (-ROR) |  | x | 0.0003 | = |  | 0 | x | 0.0003 | = |  |  | 120 Minutes | 2
SK-HEAT-W(HT) (ROR) |  | x | 0.0002 | = |  | 0 | x | 0.00045 | = |  |  | 180 Minutes | 3
SK-BEAM |  | x | 0.002 | = |  | 0 | x | 0.002 | = |  |  | 240 minutes | 4
SK-BEAM-T |  | x | 0.002 | = |  | 0 | x | 0.002 | =
SK-DUCT |  | x | 0.0003 | = |  | 0 | x | 0.0003 | =
SK-ACCLIMATE |  | x | 0.0003 | = |  | 0 | x | 0.0003 | =
SK-CONTROL |  | x | 0.000375 | = |  | 0 | x | 0.000375 | =
SK-MONITOR |  | x | 0.000375 | = |  | 0 | x | 0.000375 | =
SK-MINIMON |  | x | 0.000375 | = |  | 0 | x | 0.000375 | =
SK-PULL-SA |  | x | 0.000375 | = |  | 0 | x | 0.000375 | =
SK-PULL-DA |  | x | 0.000375 | = |  | 0 | x | 0.000375 | =
SK-MONITOR-2 |  | x | 0.00075 | = |  | 0 | x | 0.00075 | =
SK-MON-10 |  | x | 0.0035 | = |  | 0 | x | 0.0035 | =
SK-RELAY-6 |  | x | 0.00145 | = |  | 0 | x | 0.00145 | =
SK-CONTROL-6 |  | x | 0.00225 | = |  | 0 | x | 0.00225 | =
SK-RELAY |  | x | 0.000255 | = |  | 0 | x | 0.000255 | =
SK-RELAYMON-2 |  | x | 0.0013 | = |  | 0 | x | 0.024 | =
SK-ZONE |  | x | 0.00027 | = |  | 0 | x | 0.00027 | =
SK-ZONE-6 |  | x | 0.002 | = |  | 0 | x | 0.002 | =
SK-FIRE-CO |  | x | 0.0003 | = |  | 0 | x | 0.0072 | =
3. SLC Accessory Bases
B200S |  | x | 0.0003 | = |  | 0 | x | 0.0003 | =
B200S-LF |  | x | 0.0003 | = |  | 0 | x | 0.0003 | =
B200SR |  | x | 0.0003 | = |  | 0 | x | 0.0003 | =
B200SR-LF |  | x | 0.0003 | = |  | 0 | x | 0.0003 | =
B224RB |  | x | 0.0005 | = |  | 0 | x | 0.0005 | =
RTS151 |  | x | 0 | = |  | 0 | x | 0.0075 | =
RTS151KEY |  | x | 0 | = |  | 0 | x | 0.0075 | =
RA100Z |  | x | 0 | = |  | 0 | x | 0.01 | =
4. SLC Isolator Devices
SK-ISO |  | x | 0.00045 | = |  | 0 | x | 0.00045 | =
ISO-6 |  | x | 0.0027 | = |  | 0 | x | 0.102 | =
B224BI |  | x | 0.0005 | = |  | 0 | x | 0.0005 | =
5. Auxiliary Power Draw - SLC Devices
SK-CONTROL (Aux. Power) |  | x | 0.0017 | = |  | 0 | x | 0.007 | =
SK-CONTROL-6 (Aux. Power) |  | x | 0.008 | = |  | 0 | x | 0.02 | =
SK-ZONE (Aux. Power) |  | x | 0.012 | = |  | 0 | x | 0.09 | =
SK-ZONE-6 (Aux. Power) |  | x | 0.05 | = |  | 0 | x | 0.27 | =
B200S (Aux. Power) |  | x | 0.0005 | = |  | 0 | x | 0.035 | =
B200S-LF (Aux. Power) |  | x | 0.00055 | = |  | 0 | x | 0.14 | =
B200SR (Aux. Power) |  | x | 0.0005 | = |  | 0 | x | 0.035 | =
B200SR-LF (Aux. Power) |  | x | 0.001 | = |  | 0 | x | 0.125 | =
6. Accessory Modules
5860 |  | x | 0.02 | = |  | 0 | x | 0.025 | =
5824 |  | x | 0.045 | = |  | 0 | x | 0.045 | =
5496 |  | x | 0.01 | = |  | 0 | x | 0.01 | =
5895XL |  | x | 0.01 | = |  | 0 | x | 0.01 | =
6855 |  | x | 0.02 | = |  | 0 | x | 0.025 | =
6860 |  | x | 0.025 | = |  | 0 | x | 0.05 | =
5865-4 |  | x | 0.035 | = |  | 0 | x | 0.145 | =
5865-3 |  | x | 0.035 | = |  | 0 | x | 0.145 | =
5880 |  | x | 0.035 | = |  | 0 | x | 0.2 | =
5883 |  | x | 0 | = |  | 0 | x | 0.22 | =
SK-IP-2 |  | x | 0.093 | = |  | 0 | x | 0.136 | =
SK-IP-2UD |  | x | 0.098 | = |  | 0 | x | 0.155 | =
CELL-MOD |  | x | 0.055 | = |  | 0 | x | 0.1 | =
CELL-CAB-SK |  | x | 0.055 | = |  | 0 | x | 0.1 | =
WSK-WGI Aux. Power |  | x | 0.04 | = |  | 0 | x | 0.04 | =
SLC Power |  | x | 0.024 | = |  | 0 | x | 0.024 | =
SK-NIC |  | x | 0.021 | = |  | 0 | x | 0.021 | =
SK-NIC-KIT |  | x | 0.021 | = |  | 0 | x | 0.021 | =
SK-FSL |  | x | 0.079 | = |  | 0 | x | 0.079 | =
SK-FML |  | x | 0.053 | = |  | 0 | x | 0.053 | =
SK-FFT |  | x | 0.12 | = |  | 0 | x | 0.23 | =
Miscellaneous Device 3 |  | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 4 |  | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 5 |  | x | 0 | = |  | 0 | x | 0 | =
8. Notification Appliance Circuits
NAC 1 |  |  | 0 | = |  |  |  | 0 | =
NAC 2 |  |  | 0 | = |  |  |  | 0 | =
NAC 3 |  |  | 0 | = |  |  |  | 0 | =
NAC 4 |  |  | 0 | = |  |  |  | 0 | =
Total Standby Load |  |  |  |  | 0.19 | Total Alarm Load |  |  |  | 0.25
IntelliKnight 6808 Battery Calculation
Note 1: You are fully responsible for verifying these calculations.
Note 2: Use the dropdowns in the yellow cells to enter values.
Calculation in Total Sheet
Required Standby Time in Hours
24 Hours
Standby Load Current |  |  | 0.19 |  |  | x | 24 |  | = | 4.56
Required Alarm Time in Minutes
5 Minutes
Alarm Load Current (Amps) |  |  | 0.25 |  |  | x | 0.084 |  | = | 0.021
Total Current Load | [9 empty] | 4.581
Multiply by the Derating Factor | [5 empty] | 1.2 |  |  | = | 1.2
Total Ampere Hours Required | [9 empty] | 5.4972
Recommended Batteries: | [5 empty] | BAT-1270 - 7AH Batteries
Battery Check
The batteries can be charged by the 6808 Charger.
The batteries can be housed in the 6808 Cabinet.
Current Draw Check
Circuit#1 current is within the limitations of the circuit.
Circuit#2 current is within the limitations of the circuit.
Circuit#3 current is within the limitations of the circuit.
Circuit#4 current is within the limitations of the circuit.
6808 Control Panel:
The output current is within the panel's limitations.
IntelliKnight 6808 Circuit Detail
NAC 1
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
NAC 2
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
NAC 3
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
NAC 4
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
IntelliKnight 6808 EOL Voltage Drop
Starting Voltage | 20.4
Minimum Voltage @ EOL | 16
Voltage Drop Warning % | 10%
| Current Draw |  | Wire Type | Resistance |  | Length |  | Actual Resistance | Voltage @ EOL |  | Percent Drop
Circuit Name | Amps |  | AWG | Ohms/1000 ft. |  | Feet (One Way) |  | Ohms | Volts |  | Percent
NAC 1 | 0 |  | #12 Solid | 1.93 |  | 0 |  | 0 | 20.4 |  | 0%
NAC 2 | 0 |  | #12 Solid | 1.93 |  | 0 |  | 0 | 20.4 |  | 0%
NAC 3 | 0 |  | #12 Solid | 1.93 |  | 0 |  | 0 | 20.4 |  | 0%
NAC 4 | 0 |  | #12 Solid | 1.93 |  | 0 |  | 0 | 20.4 |  | 0%
Resistance Table
Wire Type |  | Resitance
AWG |  | Ohms/1000 ft.
#10 Solid |  | 1.21
#10 Stranded |  | 1.24
#12 Solid |  | 1.93
#12 Stranded |  | 1.98
#14 Solid |  | 3.07
#14 Stranded |  | 3.14
#16 Solid |  | 4.89
#16 Stranded |  | 4.99
#18 Solid |  | 7.77
#18 Stranded |  | 7.95
Note: All Resistance values are taken from Table 8 Conductor Properties of the NFPA 70 National Electrical Code. All values are for Direct Current Resistance at 75°C (167°F).
Note on H94: Select Standby Time in Hours from the dropdown list.
Note on H97: Select the Alarm Time in minutes from the dropdown list.
Note on H100: Select the Derating Factor from the dropdown list.

## 6820H
IntelliKnight 6820 Battery Calculation
| Secondary Power Source Requirements | [10 empty] | 5 Minutes | 0.084 | 24 Hours | 24
[12 empty] | 10 Minutes | 0.167 | 48 Hours | 48
| Standby Current (amps) |  |  |  |  | Secondary Alarm Current (amps) | [5 empty] | 15 Minutes | 0.25 | 60 Hours | 60
Device Type | Qty | Current Draw |  |  | Total | Qty | Current Draw |  |  | Total |  | 20 Minutes | 0.334 | 72 Hours | 72
1. Control Panel | [11 empty] | 25 Minutes | 0.417 | 90 Hours | 90
6820 Control Panel | 1 | x | 0.19 | = | 0.19 | 1 | x | 0.25 | = | 0.25 |  | 30 Minutes | 0.5 | 96 Hours | 96
2. Addressable SLC Devices | [11 empty] | 45 Minutes | 0.75 | 120 Hours | 120
SD500-AIM | 0 | x | 0.00055 | = |  | 0 | x | 0.00055 | = |  |  | 60 Minutes | 1
SD500-MIM | 0 | x | 0.00055 | = |  | 0 | x | 0.00055 | = |  |  | 90 Minutes | 1.5
SD500-ARM | 0 | x | 0.00055 | = |  | 0 | x | 0.00055 | = |  |  | 120 Minutes | 2
SD500-PS | 0 | x | 0.00055 | = |  | 0 | x | 0.00055 | = |  |  | 180 Minutes | 3
SD500-PSDA | 0 | x | 0.00055 | = |  | 0 | x | 0.00055 | = |  |  | 240 minutes | 4
SD505-HEAT | 0 | x | 0.00055 | = |  | 0 | x | 0.00055 | =
SD505-PHOTO | 0 | x | 0.00055 | = |  | 0 | x | 0.00055 | =
SD505-DTS-K | 0 | x | 0 | = |  | 0 | x | 0 | =
SD500-ANM | 0 | x | 0.00055 | = |  | 0 | x | 0.00055 | =
SD500-SDM | 0 | x | 0.00055 | = |  | 0 | x | 0.00055 | =
SD505-DUCT | 0 | x | 0.00055 | = |  | 0 | x | 0.00055 | =
SD505-DUCTR | 0 | x | 0.0005 | = |  | 0 | x | 0.00055 | =
3. SLC Accessory Bases
SD505-4AB | 0 | x | 0 | = |  | 0 | x | 0 | =
SD505-6AB | 0 | x | 0 | = |  | 0 | x | 0 | =
SD505-6RB | 0 | x | 8.2e-05 | = |  | 0 | x | 8.2e-05 | =
SD505-6SB | 0 | x | 8.2e-05 | = |  | 0 | x | 8.2e-05 | =
4. SLC Isolator Devices
SD500-LIM | 0 | x | 9.2e-05 | = |  | 0 | x | 9.2e-05 | =
SD505-6IB | 0 | x | 9.2e-05 | = |  | 0 | x | 9.2e-05 | =
5. Auxiliary Power Draw - SLC Devices
SD500-ANM (Aux. Power) | 0 | x | 0.008 | = |  | 0 | x | 0.06 | =
SD500-SDM (Aux. Power) | 0 | x | 0.02 | = |  | 0 | x | 0.106 | =
SD500-LED (Aux. Power) | 0 | x | 0.01 | = |  | 0 | x | 0.22 | =
SD505-6SB (Aux. Power) | 0 | x | 0.001 | = |  | 0 | x | 0.032 | =
6. Accessory Modules
5815XL | 0 | x | 0.055 | = |  | 0 | x | 0.055 | =
5860 | 0 | x | 0.02 | = |  | 0 | x | 0.025 | =
5860R | 0 | x | 0.02 | = |  | 0 | x | 0.025 | =
5824 | 0 | x | 0.045 | = |  | 0 | x | 0.045 | =
5496 | 0 | x | 0.01 | = |  | 0 | x | 0.01 | =
5895XL | 0 | x | 0.01 | = |  | 0 | x | 0.01 | =
5865-4 | 0 | x | 0.035 | = |  | 0 | x | 0.145 | =
5865-3 | 0 | x | 0.035 | = |  | 0 | x | 0.145 | =
5880 | 0 | x | 0.035 | = |  | 0 | x | 0.2 | =
5883 | 0 | x | 0 | = |  | 0 | x | 0.22 | =
SK-IP-2 | 0 | x | 0.093 | = |  | 0 | x | 0.136 | =
SK-IP-2UD | 0 | x | 0.098 | = |  | 0 | x | 0.155 | =
CELL-MOD | 0 | x | 0.055 | = |  | 0 | x | 0.1 | =
CELL-CAB-SK | 0 | x | 0.055 | = |  | 0 | x | 0.1 | =
SK-NIC | 0 | x | 0.021 | = |  | 0 | x | 0.021 | =
SK-NIC-KIT | 0 | x | 0.021 | = |  | 0 | x | 0.021 | =
SK-FSL | 0 | x | 0.079 | = |  | 0 | x | 0.079 | =
SK-FML | 0 | x | 0.053 | = |  | 0 | x | 0.053 | =
SK-NIC | 0 | x | 0.021 | = |  | 0 | x | 0.021 | =
SK-NIC-KIT | 0 | x | 0.021 | = |  | 0 | x | 0.021 | =
SK-FSL | 0 | x | 0.079 | = |  | 0 | x | 0.079 | =
SK-FML | 0 | x | 0.053 | = |  | 0 | x | 0.053 | =
SK-FFT | 0 | x | 0.12 | = |  | 0 | x | 0.23 | =
7. Miscellaneous Devices
Conventional Detectors | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 1 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 2 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 3 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 4 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 5 | 0 | x | 0 | = |  | 0 | x | 0 | =
8. Output Circuits
NAC 1 |  |  | 0 | = |  |  |  | 0 | =
NAC 2 |  |  | 0 | = |  |  |  | 0 | =
NAC 3 |  |  | 0 | = |  |  |  | 0 | =
NAC 4 |  |  | 0 | = |  |  |  | 0 | =
NAC 5 |  |  | 0 | = |  |  |  | 0 | =
NAC 6 |  |  | 0 | = |  |  |  | 0 | =
Total Standby Load |  |  |  |  | 0.19 | Total Alarm Load |  |  |  | 0.25
IntelliKnight 6820 Battery Calculation
Note 1: You are fully responsible for verifying these calculations.
Note 2: Use the dropdowns in the yellow cells to enter values.
Calculation in Total Sheet
Required Standby Time in Hours
24 Hours
Standby Load Current |  |  | 0.19 |  |  | x | 24 |  | = | 4.56
Required Alarm Time in Minutes
5 Minutes
Alarm Load Current (Amps) |  |  | 0.25 |  |  | x | 0.084 |  | = | 0.021
Total Current Load | [9 empty] | 4.581
Multiply by the Derating Factor | [5 empty] | 1.2 |  |  | = | 1.2
Total Ampere Hours Required | [9 empty] | 5.4972
Recommended Batteries: | [5 empty] | BAT-1270 - 7AH Batteries
Battery Check
The batteries can be charged by the 6820 Charger.
The batteries can be housed in the 6820 Cabinet.
Current Draw Check
Circuit#1 current is within the limitations of the circuit.
Circuit#2 current is within the limitations of the circuit.
Circuit#3 current is within the limitations of the circuit.
Circuit#4 current is within the limitations of the circuit.
Circuit#5 current is within the limitations of the circuit.
Circuit#6 current is within the limitations of the circuit.
6820 Control Panel:
The output current is within the panel's limitations.
IntelliKnight 6820 Circuit Detail
NAC 1
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
NAC 2
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
NAC 3
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
NAC 4
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
NAC 5
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
NAC 6
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
|  | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
IntelliKnight 6820 EOL Voltage Drop
Starting Voltage | 20.4
Minimum Voltage @ EOL | 16
Voltage Drop Warning % | 10%
| Current Draw |  | Wire Type | Resistance |  | Length |  | Actual Resistance | Voltage @ EOL |  | Percent Drop
Circuit Name | Amps |  | AWG | Ohms/1000 ft. |  | Feet (One Way) |  | Ohms | Volts |  | Percent
NAC 1 | 0 |  | #12 Solid | 1.93 |  | 0 |  | 0 | 20.4 |  | 0%
NAC 2 | 0 |  | #12 Solid | 1.93 |  | 0 |  | 0 | 20.4 |  | 0%
NAC 3 | 0 |  | #12 Solid | 1.93 |  | 0 |  | 0 | 20.4 |  | 0%
NAC 4 | 0 |  | #12 Solid | 1.93 |  | 0 |  | 0 | 20.4 |  | 0%
NAC 5 | 0 |  | #12 Solid | 1.93 |  | 0 |  | 0 | 20.4 |  | 0%
NAC 6 | 0 |  | #12 Solid | 1.93 |  | 0 |  | 0 | 20.4 |  | 0%
Resistance Table
Wire Type |  | Resitance
AWG |  | Ohms/1000 ft.
#10 Solid |  | 1.21
#10 Stranded |  | 1.24
#12 Solid |  | 1.93
#12 Stranded |  | 1.98
#14 Solid |  | 3.07
#14 Stranded |  | 3.14
#16 Solid |  | 4.89
#16 Stranded |  | 4.99
#18 Solid |  | 7.77
#18 Stranded |  | 7.95
Note: All Resistance values are taken from Table 8 Conductor Properties of the NFPA 70 National Electrical Code. All values are for Direct Current Resistance at 75°C (167°F).
Note on H83: Select Standby Time in Hours from the dropdown list.
Note on H86: Select the Alarm Time in minutes from the dropdown list.
Note on H89: Select the Derating Factor from the dropdown list.

## 6820SS
IntelliKnight 6820 Battery Calculation
| Secondary Power Source Requirements | [10 empty] | 5 Minutes | 0.084 | 24 Hours | 24
[12 empty] | 10 Minutes | 0.167 | 48 Hours | 48
| Standby Current (amps) |  |  |  |  | Secondary Alarm Current (amps) | [5 empty] | 15 Minutes | 0.25 | 60 Hours | 60
Device Type | Qty | Current Draw |  |  | Total | Qty | Current Draw |  |  | Total |  | 20 Minutes | 0.334 | 72 Hours | 72
1. Control Panel | [11 empty] | 25 Minutes | 0.417 | 90 Hours | 90
6820 Control Panel | 1 | x | 0.19 | = | 0.19 | 1 | x | 0.25 | = | 0.25 |  | 30 Minutes | 0.5 | 96 Hours | 96
2. Addressable SLC Devices | [11 empty] | 45 Minutes | 0.75 | 120 Hours | 120
SK-PHOTO (-T) |  | x | 0.0003 | = |  | 0 | x | 0.0003 | = |  |  | 60 Minutes | 1
SK-PHOTO-W (-T) |  | x | 0.0002 | = |  | 0 | x | 0.00045 | = |  |  | 90 Minutes | 1.5
SK-HEAT(-HT) (-ROR) |  | x | 0.0003 | = |  | 0 | x | 0.0003 | = |  |  | 120 Minutes | 2
SK-HEAT-W(HT) (ROR) |  | x | 0.0002 | = |  | 0 | x | 0.00045 | = |  |  | 180 Minutes | 3
SK-BEAM |  | x | 0.002 | = |  | 0 | x | 0.002 | = |  |  | 240 minutes | 4
SK-BEAM-T |  | x | 0.002 | = |  | 0 | x | 0.002 | =
SK-DUCT |  | x | 0.0003 | = |  | 0 | x | 0.0003 | =
SK-ACCLIMATE |  | x | 0.0003 | = |  | 0 | x | 0.0003 | =
SK-CONTROL |  | x | 0.000375 | = |  | 0 | x | 0.000375 | =
SK-MONITOR |  | x | 0.000375 | = |  | 0 | x | 0.000375 | =
SK-MINIMON |  | x | 0.000375 | = |  | 0 | x | 0.000375 | =
SK-PULL-SA |  | x | 0.000375 | = |  | 0 | x | 0.000375 | =
SK-PULL-DA |  | x | 0.000375 | = |  | 0 | x | 0.000375 | =
SK-MONITOR-2 |  | x | 0.00075 | = |  | 0 | x | 0.00075 | =
SK-MON-10 |  | x | 0.0035 | = |  | 0 | x | 0.0035 | =
SK-RELAY-6 |  | x | 0.00145 | = |  | 0 | x | 0.00145 | =
SK-CONTROL-6 |  | x | 0.00225 | = |  | 0 | x | 0.00225 | =
SK-RELAY |  | x | 0.000255 | = |  | 0 | x | 0.000255 | =
SK-RELAYMON-2 |  | x | 0.0013 | = |  | 0 | x | 0.024 | =
SK-ZONE |  | x | 0.00027 | = |  | 0 | x | 0.00027 | =
SK-ZONE-6 |  | x | 0.002 | = |  | 0 | x | 0.002 | =
SK-FIRE-CO |  | x | 0.0003 | = |  | 0 | x | 0.0072 | =
3. SLC Accessory Bases
B200S | 0 | x | 0.0003 | = |  | 0 | x | 0.0003 | =
B200S-LF | 0 | x | 0.0003 | = |  | 0 | x | 0.0003 | =
B200SR | 0 | x | 0.0003 | = |  | 0 | x | 0.0003 | =
B200SR-LF | 0 | x | 0.0003 | = |  | 0 | x | 0.0003 | =
B224RB | 0 | x | 0.0005 | = |  | 0 | x | 0.0005 | =
RTS151 | 0 | x | 0 | = |  | 0 | x | 0.0075 | =
RTS151KEY | 0 | x | 0 | = |  | 0 | x | 0.0075 | =
RA100Z | 0 | x | 0 | = |  | 0 | x | 0.01 | =
4. SLC Isolator Devices
SK-ISO | 0 | x | 0.00045 | = |  | 0 | x | 0.00045 | =
ISO-6 | 0 | x | 0.0027 | = |  | 0 | x | 0.102 | =
B224BI | 0 | x | 0.0005 | = |  | 0 | x | 0.0005 | =
5. Auxiliary Power Draw - SLC Devices
SK-CONTROL (Aux. Power) | 0 | x | 0.0017 | = |  | 0 | x | 0.007 | =
SK-CONTROL-6 (Aux. Power) | 0 | x | 0.008 | = |  | 0 | x | 0.02 | =
SK-ZONE (Aux. Power) | 0 | x | 0.012 | = |  | 0 | x | 0.09 | =
SK-ZONE-6 (Aux. Power) | 0 | x | 0.05 | = |  | 0 | x | 0.27 | =
B200S (Aux. Power) | 0 | x | 0.0005 | = |  | 0 | x | 0.035 | =
B200S-LF (Aux. Power) | 0 | x | 0.00055 | = |  | 0 | x | 0.14 | =
B200SR (Aux. Power) | 0 | x | 0.0005 | = |  | 0 | x | 0.035 | =
B200SR-LF (Aux. Power) | 0 | x | 0.001 | = |  | 0 | x | 0.125 | =
6. Accessory Modules
6815 | 0 | x | 0.078 | = |  | 0 | x | 0.07855 | =
5860 | 0 | x | 0.02 | = |  | 0 | x | 0.025 | =
5824 | 0 | x | 0.045 | = |  | 0 | x | 0.045 | =
5496 | 0 | x | 0.01 | = |  | 0 | x | 0.01 | =
5895XL | 0 | x | 0.01 | = |  | 0 | x | 0.01 | =
6855 | 0 | x | 0.02 | = |  | 0 | x | 0.025 | =
6860 | 0 | x | 0.025 | = |  | 0 | x | 0.05 | =
5865-4 | 0 | x | 0.035 | = |  | 0 | x | 0.145 | =
5865-3 | 0 | x | 0.035 | = |  | 0 | x | 0.145 | =
5880 | 0 | x | 0.035 | = |  | 0 | x | 0.2 | =
5883 | 0 | x | 0 | = |  | 0 | x | 0.22 | =
SK-IP-2 | 0 | x | 0.093 | = |  | 0 | x | 0.136 | =
SK-IP-2UD | 0 | x | 0.098 | = |  | 0 | x | 0.155 | =
CELL-MOD | 0 | x | 0.055 | = |  | 0 | x | 0.1 | =
CELL-CAB-SK | 0 | x | 0.055 | = |  | 0 | x | 0.1 | =
WSK-WGI Aux. Power | 0 | x | 0.04 | = |  | 0 | x | 0.04 | =
SLC Power | 0 | x | 0.024 | = |  | 0 | x | 0.024 | =
SK-NIC | 0 | x | 0.021 | = |  | 0 | x | 0.021 | =
SK-NIC-KIT | 0 | x | 0.021 | = |  | 0 | x | 0.021 | =
SK-FSL | 0 | x | 0.079 | = |  | 0 | x | 0.079 | =
SK-FML | 0 | x | 0.053 | = |  | 0 | x | 0.053 | =
SK-FFT | 0 | x | 0.12 | = |  | 0 | x | 0.23 | =
Miscellaneous Device 1 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 2 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 3 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 4 | 0 | x | 0 | = |  | 0 | x | 0 | =
8. Output Circuits
NAC 1 |  |  | 0 | = |  |  |  | 0 | =
NAC 2 |  |  | 0 | = |  |  |  | 0 | =
NAC 3 |  |  | 0 | = |  |  |  | 0 | =
NAC 4 |  |  | 0 | = |  |  |  | 0 | =
I/O 5 |  |  | 0 | = |  |  |  | 0 | =
I/O 6 |  |  | 0 | = |  |  |  | 0 | =
Total Standby Load |  |  |  |  | 0.19 | Total Alarm Load |  |  |  | 0.25
IntelliKnight 6820 Battery Calculation
Note 1: You are fully responsible for verifying these calculations.
Note 2: Use the dropdowns in the yellow cells to enter values.
Calculation in Total Sheet
Required Standby Time in Hours
24 Hours
Standby Load Current |  |  | 0.19 |  |  | x | 24 |  | = | 4.56
Required Alarm Time in Minutes
5 Minutes
Alarm Load Current (Amps) |  |  | 0.25 |  |  | x | 0.084 |  | = | 0.021
Total Current Load | [9 empty] | 4.581
Multiply by the Derating Factor | [5 empty] | 1.2 |  |  | = | 1.2
Total Ampere Hours Required | [9 empty] | 5.4972
Recommended Batteries: | [5 empty] | BAT-1270 - 7AH Batteries
Battery Check
The batteries can be charged by the 6820 Charger.
The batteries can be housed in the 6820 Cabinet.
Current Draw Check
Circuit#1 current is within the limitations of the circuit.
Circuit#2 current is within the limitations of the circuit.
Circuit#3 current is within the limitations of the circuit.
Circuit#4 current is within the limitations of the circuit.
Circuit#5 current is within the limitations of the circuit.
Circuit#6 current is within the limitations of the circuit.
6820 Control Panel:
The output current is within the panel's limitations.
IntelliKnight 6820 Circuit Detail
NAC 1
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
NAC 2
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
NAC 3
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
NAC 4
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
I/O 5
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
I/O 6
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
IntelliKnight 6820 EOL Voltage Drop
Starting Voltage | 20.4
Minimum Voltage @ EOL | 16
Voltage Drop Warning % | 10%
| Current Draw |  | Wire Type | Resistance |  | Length |  | Actual Resistance | Voltage @ EOL |  | Percent Drop
Circuit Name | Amps |  | AWG | Ohms/1000 ft. |  | Feet (One Way) |  | Ohms | Volts |  | Percent
NAC 1 | 0 |  | #14 Solid | 3.07 |  | 0 |  | 0 | 20.4 |  | 0%
NAC 2 | 0 |  | #12 Solid | 1.93 |  | 0 |  | 0 | 20.4 |  | 0%
NAC 3 | 0 |  | #12 Solid | 1.93 |  | 0 |  | 0 | 20.4 |  | 0%
NAC 4 | 0 |  | #12 Solid | 1.93 |  | 0 |  | 0 | 20.4 |  | 0%
I/O 5 | 0 |  | #12 Solid | 1.93 |  | 0 |  | 0 | 20.4 |  | 0%
I/O 6 | 0 |  | #12 Solid | 1.93 |  | 0 |  | 0 | 20.4 |  | 0%
Resistance Table
Wire Type |  | Resitance
AWG |  | Ohms/1000 ft.
#10 Solid |  | 1.21
#10 Stranded |  | 1.24
#12 Solid |  | 1.93
#12 Stranded |  | 1.98
#14 Solid |  | 3.07
#14 Stranded |  | 3.14
#16 Solid |  | 4.89
#16 Stranded |  | 4.99
#18 Solid |  | 7.77
#18 Stranded |  | 7.95
Note: All Resistance values are taken from Table 8 Conductor Properties of the NFPA 70 National Electrical Code. All values are for Direct Current Resistance at 75°C (167°F).
Note on H98: Select Standby Time in Hours from the dropdown list.
Note on H101: Select the Alarm Time in minutes from the dropdown list.
Note on H104: Select the Derating Factor from the dropdown list.

## 6820SS EVS
IntelliKnight 6820-EVS Battery Calculation
| Secondary Power Source Requirements | [10 empty] | 5 Minutes | 0.084 | 24 Hours | 24
[12 empty] | 10 Minutes | 0.167 | 48 Hours | 48
| Standby Current (amps) |  |  |  |  | Secondary Alarm Current (amps) | [5 empty] | 15 Minutes | 0.25 | 60 Hours | 60
Device Type | Qty | Current Draw |  |  | Total | Qty | Current Draw |  |  | Total |  | 20 Minutes | 0.334 | 72 Hours | 72
1. Control Panel | [11 empty] | 25 Minutes | 0.417 | 90 Hours | 90
6820 Control Panel | 1 | x | 0.19 | = | 0.19 | 1 | x | 0.25 | = | 0.25 |  | 30 Minutes | 0.5 | 96 Hours | 96
2. Addressable SLC Devices | [11 empty] | 45 Minutes | 0.75 | 120 Hours | 120
SK-PHOTO (-T) |  | x | 0.0003 | = |  | 0 | x | 0.0003 | = |  |  | 60 Minutes | 1
SK-PHOTO-W (-T) |  | x | 0.0002 | = |  | 0 | x | 0.00045 | = |  |  | 90 Minutes | 1.5
SK-HEAT(-HT) (-ROR) |  | x | 0.0003 | = |  | 0 | x | 0.0003 | = |  |  | 120 Minutes | 2
SK-HEAT-W(HT) (ROR) |  | x | 0.0002 | = |  | 0 | x | 0.00045 | = |  |  | 180 Minutes | 3
SK-BEAM |  | x | 0.002 | = |  | 0 | x | 0.002 | = |  |  | 240 minutes | 4
SK-BEAM-T |  | x | 0.002 | = |  | 0 | x | 0.002 | =
SK-DUCT |  | x | 0.0003 | = |  | 0 | x | 0.0003 | =
SK-ACCLIMATE |  | x | 0.0003 | = |  | 0 | x | 0.0003 | =
SK-CONTROL |  | x | 0.000375 | = |  | 0 | x | 0.000375 | =
SK-MONITOR |  | x | 0.000375 | = |  | 0 | x | 0.000375 | =
SK-MINIMON |  | x | 0.000375 | = |  | 0 | x | 0.000375 | =
SK-PULL-SA |  | x | 0.000375 | = |  | 0 | x | 0.000375 | =
SK-PULL-DA |  | x | 0.000375 | = |  | 0 | x | 0.000375 | =
SK-MONITOR-2 |  | x | 0.00075 | = |  | 0 | x | 0.00075 | =
SK-MON-10 |  | x | 0.0035 | = |  | 0 | x | 0.0035 | =
SK-RELAY-6 |  | x | 0.00145 | = |  | 0 | x | 0.00145 | =
SK-CONTROL-6 |  | x | 0.00225 | = |  | 0 | x | 0.00225 | =
SK-RELAY |  | x | 0.000255 | = |  | 0 | x | 0.000255 | =
SK-RELAYMON-2 |  | x | 0.0013 | = |  | 0 | x | 0.024 | =
SK-ZONE |  | x | 0.00027 | = |  | 0 | x | 0.00027 | =
SK-ZONE-6 |  | x | 0.002 | = |  | 0 | x | 0.002 | =
SK-FIRE-CO |  | x | 0.0003 | = |  | 0 | x | 0.0072 | =
3. SLC Accessory Bases
B200S |  | x | 0.0003 | = |  | 0 | x | 0.0003 | =
B200S-LF | 0 | x | 0.0003 | = |  | 0 | x | 0.0003 | =
B200SR | 0 | x | 0.0003 | = |  | 0 | x | 0.0003 | =
B200SR-LF | 0 | x | 0.0003 | = |  | 0 | x | 0.0003 | =
B224RB | 0 | x | 0.0005 | = |  | 0 | x | 0.0005 | =
RTS151 | 0 | x | 0 | = |  | 0 | x | 0.0075 | =
RTS151KEY | 0 | x | 0 | = |  | 0 | x | 0.0075 | =
RA100Z | 0 | x | 0 | = |  | 0 | x | 0.01 | =
4. SLC Isolator Devices
SK-ISO | 0 | x | 0.00045 | = |  | 0 | x | 0.00045 | =
ISO-6 | 0 | x | 0.0027 | = |  | 0 | x | 0.102 | =
B224BI | 0 | x | 0.0005 | = |  | 0 | x | 0.0005 | =
5. Auxiliary Power Draw - SLC Devices
SK-CONTROL (Aux. Power) | 0 | x | 0.0017 | = |  | 0 | x | 0.007 | =
SK-CONTROL-6 (Aux. Power) | 0 | x | 0.008 | = |  | 0 | x | 0.02 | =
SK-ZONE (Aux. Power) | 0 | x | 0.012 | = |  | 0 | x | 0.09 | =
SK-ZONE-6 (Aux. Power) | 0 | x | 0.05 | = |  | 0 | x | 0.27 | =
B200S (Aux. Power) | 0 | x | 0.0005 | = |  | 0 | x | 0.035 | =
B200S-LF (Aux. Power) | 0 | x | 0.00055 | = |  | 0 | x | 0.14 | =
B200SR (Aux. Power) | 0 | x | 0.0005 | = |  | 0 | x | 0.035 | =
B200SR-LF (Aux. Power) | 0 | x | 0.001 | = |  | 0 | x | 0.125 | =
6. Accessory Modules
6815 |  | x | 0.078 | = |  | 0 | x | 0.07855 | =
5860 | 0 | x | 0.02 | = |  | 0 | x | 0.025 | =
5824 | 0 | x | 0.045 | = |  | 0 | x | 0.045 | =
5496 |  | x | 0.01 | = |  | 0 | x | 0.01 | =
5895XL | 0 | x | 0.01 | = |  | 0 | x | 0.01 | =
6855 | 0 | x | 0.02 | = |  | 0 | x | 0.025 | =
6860 | 0 | x | 0.025 | = |  | 0 | x | 0.05 | =
5865-4 | 0 | x | 0.035 | = |  | 0 | x | 0.145 | =
5865-3 | 0 | x | 0.035 | = |  | 0 | x | 0.145 | =
5880 | 0 | x | 0.035 | = |  | 0 | x | 0.2 | =
5883 | 0 | x | 0 | = |  | 0 | x | 0.22 | =
SK-IP-2 | 0 | x | 0.093 | = |  | 0 | x | 0.136 | =
SK-IP-2UD | 0 | x | 0.098 | = |  | 0 | x | 0.155 | =
CELL-MOD | 0 | x | 0.055 | = |  | 0 | x | 0.1 | =
CELL-CAB-SK | 0 | x | 0.055 | = |  | 0 | x | 0.1 | =
WSK-WGI Aux. Power | 0 | x | 0.04 | = |  | 0 | x | 0.04 | =
SLC Power | 0 | x | 0.024 | = |  | 0 | x | 0.024 | =
SK-NIC | 0 | x | 0.021 | = |  | 0 | x | 0.021 | =
SK-NIC-KIT | 0 | x | 0.021 | = |  | 0 | x | 0.021 | =
SK-FSL | 0 | x | 0.079 | = |  | 0 | x | 0.079 | =
SK-FML | 0 | x | 0.053 | = |  | 0 | x | 0.053 | =
SK-FFT | 0 | x | 0.12 | = |  | 0 | x | 0.23 | =
EVS-INT50W @25V |  | x | 0.052 | = |  | 0 | x | 0.275 | =
EVS-INT50W WATTS USED @25V |  | x | 0 | = |  | 0 | x | 0.0513 | =
EVS-INT50W @70V |  | x | 0.052 | = |  | 0 | x | 0.31 | =
EVS-INT50W WATTS USED @70V | 0 | x | 0 | = |  | 0 | x | 0.0518 | =
EVS-50W |  | x | 0.01 | = |  | 0 | x | 0.01 | =
EVS-100W |  | x | 0.01 | = |  | 0 | x | 0.01 | =
EVC-100WBU |  | x | 0.01 | = |  | 0 | x | 0.01 | =
EVS-125W |  | x | 0.01 | = |  | 0 | x | 0.01 | =
EVS-VCM |  | x | 0.07 | = |  | 0 | x | 0.1 | =
EVS-SW24 |  | x | 0.01 | = |  | 0 | x | 0.025 | =
EVS-LOC |  | x | 0.1 | = |  | 0 | x | 0.15 | =
EVS-RCU | 0 | x | 0.09 | = |  | 0 | x | 0.125 | =
Miscellaneous Device 1 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 2 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 3 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 4 | 0 | x | 0 | = |  | 0 | x | 0 | =
8. Output Circuits
NAC 1 |  |  | 0 | = |  |  |  | 3 | = | 3
NAC 2 |  |  | 0 | = |  |  |  | 0 | =
NAC 3 |  |  | 0 | = |  |  |  | 0 | =
NAC 4 |  |  | 0 | = |  |  |  | 0 | =
I/O 5 |  |  | 0 | = |  |  |  | 0 | =
I/O 6 |  |  | 0 | = |  |  |  | 0 | =
Total Standby Load |  |  |  |  | 0.19 | Total Alarm Load |  |  |  | 3.25
IntelliKnight 6820-EVS Battery Calculation
Note 1: You are fully responsible for verifying these calculations.
Note 2: Use the dropdowns in the yellow cells to enter values.
Calculation in Total Sheet
Required Standby Time in Hours
24 Hours
Standby Load Current |  |  | 0.19 |  |  | x | 24 |  | = | 4.56
Required Alarm Time in Minutes
5 Minutes
Alarm Load Current (Amps) |  |  | 3.25 |  |  | x | 0.084 |  | = | 0.273
Total Current Load | [9 empty] | 4.833
Multiply by the Derating Factor | [5 empty] | 1.2 |  |  | = | 1.2
Total Ampere Hours Required | [9 empty] | 5.7996
Recommended Batteries: | [5 empty] | BAT-1270 - 7AH Batteries
Battery Check
The batteries can be charged by the 6820-EVS Charger.
The batteries can be housed in the 6820-EVS Cabinet.
Current Draw Check
Circuit#1 current is within the limitations of the circuit.
Circuit#2 current is within the limitations of the circuit.
Circuit#3 current is within the limitations of the circuit.
Circuit#4 current is within the limitations of the circuit.
Circuit#5 current is within the limitations of the circuit.
Circuit#6 current is within the limitations of the circuit.
6820 Control Panel:
The output current is within the panel's limitations.
IntelliKnight 6820-EVS Circuit Detail
NAC 1
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 1 | x | 3 | = | 3
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 3
NAC 2
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
NAC 3
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
NAC 4
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
I/O 5
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
I/O 6
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
IntelliKnight 6820-EVS EOL Voltage Drop
Starting Voltage | 20.4
Minimum Voltage @ EOL | 16
Voltage Drop Warning % | 10%
| Current Draw |  | Wire Type | Resistance |  | Length |  | Actual Resistance | Voltage @ EOL |  | Percent Drop
Circuit Name | Amps |  | AWG | Ohms/1000 ft. |  | Feet (One Way) |  | Ohms | Volts |  | Percent
NAC 1 | 3 |  | #14 Solid | 3.07 |  | 0 |  | 0 | 20.4 |  | 0%
NAC 2 | 0 |  | #12 Solid | 1.93 |  | 0 |  | 0 | 20.4 |  | 0%
NAC 3 | 0 |  | #12 Solid | 1.93 |  | 0 |  | 0 | 20.4 |  | 0%
NAC 4 | 0 |  | #12 Solid | 1.93 |  | 0 |  | 0 | 20.4 |  | 0%
I/O 5 | 0 |  | #12 Solid | 1.93 |  | 0 |  | 0 | 20.4 |  | 0%
I/O 6 | 0 |  | #12 Solid | 1.93 |  | 0 |  | 0 | 20.4 |  | 0%
Resistance Table
Wire Type |  | Resitance
AWG |  | Ohms/1000 ft.
#10 Solid |  | 1.21
#10 Stranded |  | 1.24
#12 Solid |  | 1.93
#12 Stranded |  | 1.98
#14 Solid |  | 3.07
#14 Stranded |  | 3.14
#16 Solid |  | 4.89
#16 Stranded |  | 4.99
#18 Solid |  | 7.77
#18 Stranded |  | 7.95
Note: All Resistance values are taken from Table 8 Conductor Properties of the NFPA 70 National Electrical Code. All values are for Direct Current Resistance at 75°C (167°F).
Note on H110: Select Standby Time in Hours from the dropdown list.
Note on H113: Select the Alarm Time in minutes from the dropdown list.
Note on H116: Select the Derating Factor from the dropdown list.

## 6820-EVSH
IntelliKnight 6820-EVS Battery Calculation
| Secondary Power Source Requirements | [10 empty] | 5 Minutes | 0.084 | 24 Hours | 24
[12 empty] | 10 Minutes | 0.167 | 48 Hours | 48
| Standby Current (amps) |  |  |  |  | Secondary Alarm Current (amps) | [5 empty] | 15 Minutes | 0.25 | 60 Hours | 60
Device Type | Qty | Current Draw |  |  | Total | Qty | Current Draw |  |  | Total |  | 20 Minutes | 0.334 | 72 Hours | 72
1. Control Panel | [11 empty] | 25 Minutes | 0.417 | 90 Hours | 90
6820 Control Panel | 1 | x | 0.275 | = | 0.275 | 1 | x | 0.44 | = | 0.44 |  | 30 Minutes | 0.5 | 96 Hours | 96
2. Addressable SLC Devices | [11 empty] | 45 Minutes | 0.75 | 120 Hours | 120
SD500-AIM | 0 | x | 0.00055 | = |  | 0 | x | 0.00055 | = |  |  | 60 Minutes | 1
SD500-MIM | 0 | x | 0.00055 | = |  | 0 | x | 0.00055 | = |  |  | 90 Minutes | 1.5
SD500-ARM | 0 | x | 0.00055 | = |  | 0 | x | 0.00055 | = |  |  | 120 Minutes | 2
SD500-PS | 0 | x | 0.00055 | = |  | 0 | x | 0.00055 | = |  |  | 180 Minutes | 3
SD500-PSDA | 0 | x | 0.00055 | = |  | 0 | x | 0.00055 | = |  |  | 240 minutes | 4
SD505-HEAT | 0 | x | 0.00055 | = |  | 0 | x | 0.00055 | =
SD505-PHOTO | 0 | x | 0.00055 | = |  | 0 | x | 0.00055 | =
SD505-DTS-K | 0 | x | 0 | = |  | 0 | x | 0 | =
SD500-ANM | 0 | x | 0.00055 | = |  | 0 | x | 0.00055 | =
SD500-SDM | 0 | x | 0.00055 | = |  | 0 | x | 0.00055 | =
SD505-DUCT | 0 | x | 0.00055 | = |  | 0 | x | 0.00055 | =
SD505-DUCTR | 0 | x | 0.0005 | = |  | 0 | x | 0.00055 | =
3. SLC Accessory Bases
SD505-4AB | 0 | x | 0 | = |  | 0 | x | 0 | =
SD505-6AB | 0 | x | 0 | = |  | 0 | x | 0 | =
SD505-6RB | 0 | x | 8.2e-05 | = |  | 0 | x | 8.2e-05 | =
SD505-6SB | 0 | x | 8.2e-05 | = |  | 0 | x | 8.2e-05 | =
4. SLC Isolator Devices
SD500-LIM | 0 | x | 9.2e-05 | = |  | 0 | x | 9.2e-05 | =
SD505-6IB | 0 | x | 9.2e-05 | = |  | 0 | x | 9.2e-05 | =
5. Auxiliary Power Draw - SLC Devices
SD500-ANM (Aux. Power) | 0 | x | 0.008 | = |  | 0 | x | 0.06 | =
SD500-SDM (Aux. Power) | 0 | x | 0.02 | = |  | 0 | x | 0.106 | =
SD500-LED (Aux. Power) | 0 | x | 0.01 | = |  | 0 | x | 0.22 | =
SD505-6SB (Aux. Power) | 0 | x | 0.001 | = |  | 0 | x | 0.032 | =
6. Accessory Modules
5815XL | 0 | x | 0.055 | = |  | 0 | x | 0.055 | =
5860 | 0 | x | 0.02 | = |  | 0 | x | 0.025 | =
5860R | 0 | x | 0.02 | = |  | 0 | x | 0.025 | =
5824 | 0 | x | 0.045 | = |  | 0 | x | 0.045 | =
5496 | 0 | x | 0.01 | = |  | 0 | x | 0.01 | =
5895XL | 0 | x | 0.01 | = |  | 0 | x | 0.01 | =
5865-4 | 0 | x | 0.035 | = |  | 0 | x | 0.145 | =
5865-3 | 0 | x | 0.035 | = |  | 0 | x | 0.145 | =
5880 | 0 | x | 0.035 | = |  | 0 | x | 0.2 | =
5883 | 0 | x | 0 | = |  | 0 | x | 0.22 | =
SK-IP-2 | 0 | x | 0.093 | = |  | 0 | x | 0.136 | =
SK-IP-2UD | 0 | x | 0.098 | = |  | 0 | x | 0.155 | =
CELL-MOD | 0 | x | 0.055 | = |  | 0 | x | 0.1 | =
CELL-CAB-SK | 0 | x | 0.055 | = |  | 0 | x | 0.1 | =
SK-NIC | 0 | x | 0.021 | = |  | 0 | x | 0.021 | =
SK-NIC-KIT | 0 | x | 0.021 | = |  | 0 | x | 0.021 | =
SK-FSL | 0 | x | 0.079 | = |  | 0 | x | 0.079 | =
SK-FML | 0 | x | 0.053 | = |  | 0 | x | 0.053 | =
SK-FFT | 0 | x | 0.12 | = |  | 0 | x | 0.23 | =
7. Voice Amplifiers and Accessories
EVS-50W | 0 | x | 0.01 | = |  | 0 | x | 0.01 | =
EVS-INT50W @ 25V |  | x | 0.052 | = |  | 0 | x | 0.275 | =
Total Watts Used 25 volts |  | x | 0 | = |  | 0 | x | 0.0513 | =
EVS-INT50W @ 70V |  | x | 0.052 | = |  | 0 | x | 0.31 | =
Total Watts Used 70 volts |  | x | 0 | = |  | 0 | x | 0.0518 | =
EVS-100W | 0 | x | 0.01 | = |  | 0 | x | 0.01 | =
EVS-125W | 0 | x | 0.01 | = |  | 0 | x | 0.01 | =
EVS-VCM | 1 | x | 0.07 | = | 0.07 | 1 | x | 0.1 | = | 0.1
EVS-SW24 | 0 | x | 0.01 | = |  | 0 | x | 0.025 | =
EVS-RCU | 0 | x | 0.09 | = |  | 0 | x | 0.125 | =
8. Miscellaneous Devices
Conventional Detectors | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 1 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 2 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 3 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 4 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 5 | 0 | x | 0 | = |  | 0 | x | 0 | =
9. Output Circuits
NAC 1 |  |  | 0 | = |  |  |  | 0 | =
NAC 2 |  |  | 0 | = |  |  |  | 0 | =
NAC 3 |  |  | 0 | = |  |  |  | 0 | =
NAC 4 |  |  | 0 | = |  |  |  | 0 | =
NAC 5 |  |  | 0 | = |  |  |  | 0 | =
NAC 6 |  |  | 0 | = |  |  |  | 0 | =
Total Standby Load |  |  |  |  | 0.345 | Total Alarm Load |  |  |  | 0.54
IntelliKnight 6820-EVS Battery Calculation
Note 1: You are fully responsible for verifying these calculations.
Note 2: Use the dropdowns in the yellow cells to enter values.
Calculation in Total Sheet
Required Standby Time in Hours
24 Hours
Standby Load Current |  |  | 0.345 |  |  | x | 24 |  | = | 8.28
Required Alarm Time in Minutes
5 Minutes
Alarm Load Current (Amps) |  |  | 0.54 |  |  | x | 0.084 |  | = | 0.04536
Total Current Load | [9 empty] | 8.3254
Multiply by the Derating Factor | [5 empty] | 1.2 |  |  | = | 1.2
Total Ampere Hours Required | [9 empty] | 9.9904
Recommended Batteries: | [5 empty] | BAT-12120 - 12AH Batteries
Battery Check
The batteries can be charged by the 6820-EVS Charger.
The batteries can be housed in the 6820-EVS Cabinet.
Current Draw Check
Circuit#1 current is within the limitations of the circuit.
Circuit#2 current is within the limitations of the circuit.
Circuit#3 current is within the limitations of the circuit.
Circuit#4 current is within the limitations of the circuit.
Circuit#5 current is within the limitations of the circuit.
Circuit#6 current is within the limitations of the circuit.
6820-EVS Control Panel:
The output current is within the panel's limitations.
IntelliKnight 6820-EVS Circuit Detail
NAC 1
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
NAC 2
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
NAC 3
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
NAC 4
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
NAC 5
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
NAC 6
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
IntelliKnight 6820-EVS EOL Voltage Drop
Starting Voltage | 20.4
Minimum Voltage @ EOL | 16
Voltage Drop Warning % | 10%
| Current Draw |  | Wire Type | Resistance |  | Length |  | Actual Resistance | Voltage @ EOL |  | Percent Drop
Circuit Name | Amps |  | AWG | Ohms/1000 ft. |  | Feet (One Way) |  | Ohms | Volts |  | Percent
NAC 1 | 0 |  | #12 Solid | 1.93 |  | 0 |  | 0 | 20.4 |  | 0%
NAC 2 | 0 |  | #12 Solid | 1.93 |  | 0 |  | 0 | 20.4 |  | 0%
NAC 3 | 0 |  | #12 Solid | 1.93 |  | 0 |  | 0 | 20.4 |  | 0%
NAC 4 | 0 |  | #12 Solid | 1.93 |  | 0 |  | 0 | 20.4 |  | 0%
NAC 5 | 0 |  | #12 Solid | 1.93 |  | 0 |  | 0 | 20.4 |  | 0%
NAC 6 | 0 |  | #12 Solid | 1.93 |  | 0 |  | 0 | 20.4 |  | 0%
Resistance Table
Wire Type |  | Resitance
AWG |  | Ohms/1000 ft.
#10 Solid |  | 1.21
#10 Stranded |  | 1.24
#12 Solid |  | 1.93
#12 Stranded |  | 1.98
#14 Solid |  | 3.07
#14 Stranded |  | 3.14
#16 Solid |  | 4.89
#16 Stranded |  | 4.99
#18 Solid |  | 7.77
#18 Stranded |  | 7.95
Note: All Resistance values are taken from Table 8 Conductor Properties of the NFPA 70 National Electrical Code. All values are for Direct Current Resistance at 75°C (167°F).
Note on H90: Select Standby Time in Hours from the dropdown list.
Note on H93: Select the Alarm Time in minutes from the dropdown list.
Note on H96: Select the Derating Factor from the dropdown list.